## Refrigerants(ASHRAE34 ISO 817)
Refrigerants designated by ASHRAE 34 or by ISO 817
March 2020 | This list is not intended to be complete or definitive. Please refer to the latest edition of ASHRAE Standard 34 and all published addenda or the latest edition of ISO 817 and its amendments for complete information on refrigerant designations and safety classifications. | see notes on refrigerant type
Number | Refrigerant Composition (Mass % ) | Refrigerant Type
Zeotropes
400 | R-12/114 (must be specified) (50.0/50.0) (60.0/40.0) | CFC
401A | R-22/152a/124 (53.0/13.0/34.0) | HCFC
401B | R-22/152a/124 (61.0/11.0/28.0 | HCFC
401C | R-22/152a/124 (33.0/15.0/52.0) | HCFC
402A | R-125/290/22 (60.0/2.0/38.0) | HCFC
402B | R-125/290/22 (38.0/2.0/60.0) | HCFC
403A | R-290/22/218 (5.0/75.0/20.0) | HCFC
403B | R-290/22/218 (5.0/56.0/39.0) | HCFC
404A | R-125/143a/134a (44.0/52.0/4.0) | HFC
405A | R-22/152a/142b/C318 (45.0/7.0/5.5/42.5) | HCFC
406A | R-22/600a/142b (55.0/4.0/41.0) | HCFC
407A | R-32/125/134a (20.0/40.0/40.0) | HFC
407B | R-32/125/134a (10.0/70.0/20.0) | HFC
407C | R-32/125/134a (23.0/25.0/52.0) | HFC
407D | R-32/125/134a (15.0/15.0/70.0) | HFC
407E | R-32/125/134a (25.0/15.0/60.0) | HFC
407F | R-32/125/134a (30.0/30.0/40.0) | HFC
407G | R-32/125/134a (2.5/2.5/95.0) | HFC
407H | R-32/125/134a (32.5/15.0/52.5) | HFC
408A | R-125/143a/22 (7.0/46.0/47.0) | HCFC
409A | R-22/124/142b (60.0/25.0/15.0) | HCFC
409B | R-22/124/142b (65.0/25.0/10.0) | HCFC
410A | R-32/125 (50.0/50.0) | HFC
410B | R-32/125 (45.0/55.0) | HFC
411A | R-1270/22/152a) (1.5/87.5/11.0) | HCFC
411B | R-1270/22/152a (3.0/94.0/3.0) | HCFC
412A | R-22/218/143b (70.0/5.0/25.0) | HCFC
413A | R-218/134a/600a (9.0/88.0/3.0) | PFC/HFC
414A | R-22/124/600a/142b (51.0/28.5/4.0/16.5) | HCFC
414B | R-22/124/600a/142b (50.0/39.0/1.5/9.5) | HCFC
415A | R-22/152a (82.0/18.0) | HCFC
415B | R-22/152a (25.0/75.0) | HCFC
416A | R-134a/124/600 (59.0/39.5/1.5) | HCFC
417A | R-125/134a/600 (46.6/50.0/3.4) | HFC
417B | R-125/134a/600 (79.0/18.3/2.7) | HFC
417C | R-125/134a/600 (19.5/78.8/1.7) | HFC
418A | R-290/22/152a (1.5/96.0/2.5) | HCFC
419A | R-125/134a/E170 (77.0/19.0/4.0) | HFC
419B | R-125/134a/E170 (48.5/48.0/3.5) | HFC
420A | R-134a/142b (88.0/12.0) | HCFC
421A | R-125/134a (58.0/42.0) | HFC
421B | R-125/134a (85.0/15.0) | HFC
422A | R-125/134a/600a (85.1/11.5/3.4) | HFC
422B | R-125/134a/600a (55.0/42.0/3.0) | HFC
422C | R-125/134a/600a (82.0/15.0/3.0) | HFC
422D | R-125/134a/600a (65.1/31.5/3.4) | HFC
422E | R-125/134a/600a (58.0/39.3/2.7) | HFC
423A | R-134a/227ea (52.5/47.5) | HFC
424A | R-125/134a/600a/600/601a (50.5/47.0/0.9/1.0/0.6) | HFC
425A | R-32/134a/227ea (18.5/69.5/12) | HFC
426A | R-125/134a/600/601a (5.1/93.0/1.3/0.6) | HFC
427A | R-32/125/143a/134a (15.0/25.0/10.0/50.0) | HFC
428A | R-125/143a/290/600a (77.5/20.0/0.6/1.9) | HFC
429A | R-E170/152a/600a (60.0/10.0/30.0) | HC/HFC
430A | R-152a/600a (76.0/24.0) | HC/HFC
431A | R-290/152a (71.0/29.0) | HC/HFC
432A | R-1270/E170 (80.0/20.0) | HC
433A | R-1270/290 (30.0/70.0) | HC
433B | R-1270/290 (5.0/95.0) | HC
433C | R-1270/290 (25.0/75.0) | HC
434A | R-125/143a/134a/600a | HFC
435A | R-E170/152a (80.0/20.0) | HC/HFC
436A | R-290/600a (56.0/44.0) | HC
436B | R-290/600a (52.0/48.0) | HC
437A | R-125/134a/600/601 (19.5/78.5/1.4/0.6) | HFC
438A | R-32/125/134a/600/601a (8.5/45.0/44.2/1.7/0.6) | HFC
439A | R-32/125/600a (50.0/47.0/3.0) | HFC
440A | R-290/134a/152a (0.6/1.6/97.8) | HFC
441A | R-170/290/600a/600 (3.1/54.8/6.0/36.1) | HC
442A | R-32/125/134a/152a/227ea (31.0/31.0/30.0/3.0/5.0) | HFC
443A | R-1270/290/600a (55.0/40.0/5.0) | HC
444A | R-32/152a/1234ze(E) (12.0/5.0/83.0) | HFC/HFO
444B | R-32/152a/1234ze(E) (41.5/10.0/48.5) | HFC/HFO
445A | R-744/134a/1234ze(E) (6.0/9.0/85.0) | HFC/HFO
446A | R-32/1234ze(E)/600 (68.0/29.0/3.0) | HFC/HFO
447A | R-32/125/1234ze(E) (68.0/3.5/28.5) | HFC/HFO
447B | R-32/125/1234ze (E) (68.0/8.0/24.0) | HFC/HFO
448A | R-32/125/1234yf/134a/1234ze(E) (26.0/26.0/20.0/21.0/7.0) | HFC/HFO
449A | R-32 /125 /1234yf /134a (24.3/24.7/25.3/25.7) | HFC/HFO
449B | R-32/125/1234yf/134a (25.2/24.3/23.2/27.3) | HFC/HFO
449C | R-32/125/1234yf/134a (20.0/20.0/31.0/29.0) | HFC/HFO
450A | R-134a/1234ze(E) (42.0/58.0) | HFC/HFO
451A | R-1234yf/134a (89.8/10.2) | HFC/HFO
451B | R-1234yf/134a (88.8/11.2) | HFC/HFO
452A | R-32/125/1234yf (11.0/59.0/30.0 | HFC/HFO
452B | R-32/125/1234yf (67.0/7.0/26.0) | HFC/HFO
452C | R-32/125/1234yf (12.5/61.0/26.5) | HFC/HFO
453A | R-32/125/134a/227ea/600/601a (20.0/20.0/53.8/5.0/0.6/0.6) | HFC
454A | R-32/1234yf (35.0/65.0) | HFC/HFO
454B | R-32/1234yf (68.9/31.1) | HFC/HFO
454C | R-32/1234yf (21.5/78.5) | HFC/HFO
455A | R-744/32/1234yf (3.0/21.5/75.5) | HFC/HFO
456A | R-32/134a/1234ze(E) (6.0/45.0/49.0) | HFC/HFO
457A | R-32/1234yf/152a (18.0/70.0/12.0) | HFC/HFO
458A | R-32/125/134a/227ea/236fa (20.5/4.0/61.4/13.5/0.6) | HFC
459A | R-32/1234yf/1234ze(E) (68.0/26.0/6.0) | HFC/HFO
459B | R-32/1234yf/1234ze(E) (21.0/69.0/10.0) | HFC/HFO
460A | R-32/125/134a/1234ze(E) (12.0/52.0/14.0/22.0) | HFC/HFO
460B | R-32/125/134a/1234ze(E) (28.0/25.0/20.0/27.0) | HFC/HFO
460C | R-32/125/134a/1234ze(E) (2.5/2.5/46.0/49.0) | HFC/HFO
461A | R-125/143a/134a/227ea/600a (55.0/5.0/32.0/5.0/3.0) | HFC
462A | R-32/125/143a/134a/600 (9.0/42.0/2.0/44.0/3.0) | HFC
463A | R-744/32/125/1234yf/134a (6/36/30/14/14) | HFC/HFO
464A | R-32/125/1234ze(E)/227ea (27/27/40/6) | HFC/HFO
465A | R-32/290/1234yf (21.0/7.9/71.1) | HFC/HFO
466A | R-32/125/13I1 (49.0/11.5/39.5) | HFC/IFC
467A | R-32/125/134a/600a (22.0/5.0/72.4/0.6) | HFC/HC
468A | R-1132a/32/1234yf (3.5/21.5/75.0) | HFC/HFO
469A | R-744/32/125 (35.0/32.5/32.5) | HFC
470A | R-744/32/125/134a/1234ze(E)/227ea (10/17/19/7/44/3) | HFC/HFO
470B | R-744/32/125/134a/1234ze(E)/227ea (10/11.5/11.5/3/57/7) | HFC/HFO
Azeotropes
500 | R-12/152a (73.8/26.2) | CFC
501 | R-22/12 (75.0/25.0) | CFC
502 | R-22/115 (48.8/51.2) | CFC
503 | R-23/13 (40.1/59.9) | CFC
504 | R-32/115 (48.2/51.8) | CFC
505 | R-12/31 (78.0/22.0) | CFC
506 | R-31/114 (55.1/44.9) | CFC
507A | R-125/143a (50.0/50.0) | HFC
508A | R-23/116 (39.0/61.0) | PFC/HFC
508B | R-23/116 (46.0/54.0) | PFC/HFC
509A | R-22/218 (44.0/56.0) | HCFC
510A | R-E170/600a (88.0/12.0) | HC
511A | R-290/E170 (95.0/5.0) | HC
512A | R-134a/152a (5.0/95.0) | HFC
513A | R-1234yf/134a (56.0/44.0) | HFC/HFO
513B | R-1234yf/134a (58.5/41.5) | HFC/HFO
514A | R-1336mzz(Z)/1130(E) (74.7/25.3) | HFO/HCO
515A | R-1234ze (E)/227ea (88.0/12.0) | HFC/HFO
515B | R-1234ze (E)/227ea (91.1/8.9) | HFC/HFO
516A | R-1234yf/134a/152a (77.5/8.5/14.0) | HFC/HFO
Notes on refrigerant type: Any refrigerant containing CFC is categorised as a CFC. Similarly for HCFCs. All refrigerants (highlighted in orange) containing ozone depleting substances are banned in the EU. Refrigerants categorised as HCs contain HCs and/or HC ethers. The safety properties( flammability) of refrigerants categorised as HC/HFC are determined by the HCs. Some refrigerants contain only small quantities of HCs and are not categorised as HCs in this table. All HFC, HC/HFC, PFC/HFC, HFC/HFO and HFC/IFC refrigerants (highlighted in yellow) are subject to the F-Gas Regulation. HFC/HFO and HFC/IFC refrigerants typically have lower GWPs that the HFCs they are intended to replace. HCO is hydrochloro-olefin. R-514A is not subject to the F-Gas Regulation except for the HFO component which is subject to reporting.

## F-Gas R-safety GWP applications
Refrigerants subject to the F-Gas Regulation 517/2014
March 2020 | This list is not intended to be complete or definitive. Please refer to the latest edition of ASHRAE Standard 34 and all published addenda or the latest edition of ISO 817 and its amendments for complete information on refrigerant designations and safety classifications. | see notes on refrigerant type
Number | Refrigerant Composition (Mass % ) | Refrigerant Type | ASHRAE Safety Classification | GWPs |  | Applications
|  |  |  | F-Gas AR4 | AR5 | brief summary consult supplier for further information on applications and use
Zeotropes
404A | R-125/143a/134a (44.0/52.0/4.0) | HFC | A1 | 3921.6 | 3942.8 | medium and low temperature commercial refrigeration;F-Gas Regulation use restrictions (GWP >2500)
407A | R-32/125/134a (20.0/40.0/40.0) | HFC | A1 | 2107 | 1923.4 | medium and low temperature commercial refrigeration
407B | R-32/125/134a (10.0/70.0/20.0) | HFC | A1 | 2803.5 | 2546.7 | medium and low temperature commercial refrigeration;F-Gas Regulation use restrictions (GWP >2500)
407C | R-32/125/134a (23.0/25.0/52.0) | HFC | A1 | 1773.85 | 1624.21 | air-conditioning units heat-pumps, chillers, industrial and commercial medium temperature refrigeration
407D | R-32/125/134a (15.0/15.0/70.0) | HFC | A1 | 1627.25 | 1487.05 | transport refrigeration
407E | R-32/125/134a (25.0/15.0/60.0) | HFC | A1 | 1551.75 | 1424.75 | air-conditioning units
407F | R-32/125/134a (30.0/30.0/40.0) | HFC | A1 | 1824.5 | 1674.1 | medium and low temperature commercial refrigeration
407G | R-32/125/134a (2.5/2.5/95.0) | HFC | A1 | 1462.875 | 1331.175 | similar to R-134a with higher capacity
407H | R-32/125/134a (32.5/15.0/52.5) | HFC | A1 | 1495.125 | 1378.025 | medium and low temperature commercial refrigeration
410A | R-32/125 (50.0/50.0) | HFC | A1 | 2087.5 | 1923.5 | air-conditioning units heat pumps; cold storage; industrial and commercial and low temperature refrigeration
410B | R-32/125 (45.0/55.0) | HFC | A1 | 2228.75 | 2048.15 | similar properties to R-410A but R-410A dominates commercially
413A | R-218/134a/600a (9.0/88.0/3.0) | PFC/HFC | A2 | 2053.19 | 1945.09 | retrofit refrigerant replacement for R-12 in some air-conditioning systems and medium and high temperature refrigeration
417A | R-125/134a/600 (46.6/50.0/3.4) | HFC | A1 | 2346.136 | 2127.356 | replacement for R-22
417B | R-125/134a/600 (79.0/18.3/2.7) | HFC | A1 | 3026.798 | 2742.308 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
417C | R-125/134a/600 (19.5/78.8/1.7) | HFC | A1 | 1809.408 | 1642.618 | replacement for R-22
419A | R-125/134a/E170 (77.0/19.0/4.0) | HFC | A2 | 2966.7 | 2687.94 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
419B | R-125/134a/E170 (48.5/48.0/3.5) | HFC | A2 | 2383.9 | 2161.485 | replacement for R-22
421A | R-125/134a (58.0/42.0) | HFC | A1 | 2630.6 | 2384.6 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
421B | R-125/134a (85.0/15.0) | HFC | A1 | 3189.5 | 2889.5 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
422A | R-125/134a/600a (85.1/11.5/3.4) | HFC | A1 | 3143.052 | 2847.272 | similar properties to R-404A; F-Gas Regulation use restrictions (GWP >2500)
422B | R-125/134a/600a (55.0/42.0/3.0) | HFC | A1 | 2525.69 | 2289.59 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
422C | R-125/134a/600a (82.0/15.0/3.0) | HFC | A1 | 3084.59 | 2794.49 | replacement for R-22 in low/medium temperature refrigeration. F-Gas Regulation use restrictions (GWP >2500)
422D | R-125/134a/600a (65.1/31.5/3.4) | HFC | A1 | 2729.052 | 2473.272 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
422E | R-125/134a/600a (58.0/39.3/2.7) | HFC | A1 | 2592.071 | 2349.581 | replacement for R-22; F-Gas Regulation use restrictions (GWP >2500)
423A | R-134a/227ea (52.5/47.5) | HFC | A1 | 2280.25 | 2273.75 | non-flammable retrofit replacement for R12 in centrifugal chillers
424A | R-125/134a/600a/600/601a (50.5/47.0/0.9/1.0/0.6) | HFC | A1 | 2439.697 | 2211.947 | non-flammable retrofit replacement for R-22 in medium and high temperature air-conditioning and refrigeration systems
425A | R-32/134a/227ea (18.5/69.5/12) | HFC | A1 | 1505.125 | 1430.745 | non-flammable replacement for R-22
426A | R-125/134a/600/601a (5.1/93.0/1.3/0.6) | HFC | A1 | 1508.482 | 1370.752 | non-flammable retrofit replacement for R-12 in medium temperature refrigeration systems
427A | R-32/125/143a/134a (15.0/25.0/10.0/50.0) | HFC | A1 | 2138.25 | 2024.05 | non-flammable replacement for R-22
428A | R-125/143a/290/600a (77.5/20.0/0.6/1.9) | HFC | A1 | 3606.575 | 3416.825 | non-flammable replacement for R-502 and R-22 in low temperature industrial refrigeration. F-Gas Regulation use restrictions (GWP >2500)
429A | R-E170/152a/600a (60.0/10.0/30.0) | HC/HFC | A3 | 13.3 | 15.3 | highly flammable alternative to R-134a for small hermetic systems
430A | R-152a/600a (76.0/24.0) | HC/HFC | A3 | 94.96 | 105.6 | highly flammable alternative to R-134a for small hermetic systems
431A | R-290/152a (71.0/29.0) | HC/HFC | A3 | 38.09 | 42.15 | highly flammable alternative to R-22 for air-conditioning systems and heat pumps
434A | R-125/143a/134a/600a | HFC | A1 | 3245.484 | 3075.524 | retrofit replacement for R-22 in medium and high temperature refrigeration. F-Gas Regulation use restrictions (GWP >2500)
435A | R-E170/152a (80.0/20.0) | HC/HFC | A3 | 24.8 | 28.4 | highly flammable alternative to R-134a for small hermetic systems
437A | R-125/134a/600/601 (19.5/78.5/1.4/0.6) | HFC | A1 | 1805.136 | 1638.736 | non-flammable retrofit refrigerant replacement for R-500 and R-12 in medium and high temperature refrigeration
438A | R-32/125/134a/600/601a (8.5/45.0/44.2/1.7/0.6) | HFC | A1 | 2264.533 | 2058.743 | non-flammable replacement for R-22
439A | R-32/125/600a (50.0/47.0/3.0) | HFC | A2 | 1982.59 | 1828.49 | retrofit replacement for R-22
440A | R-290/134a/152a (0.6/1.6/97.8) | HFC | A2 | 144.17 | 155.782 | retrofit replacement for R-134a
442A | R-32/125/134a/152a/227ea (31.0/31.0/30.0/3.0/5.0) | HFC | A1 | 1887.97 | 1754.21 | non-flammable retrofit replacement for R-22, R-404A and R-507 in low, medium and high temperature refrigeration
444A | R-32/152a/1234ze(E) (12.0/5.0/83.0) | HFC/HFO | A2L | 93.01 | 88.97 | replacement for R-134a in medium temperature commercial refrigeration
444B | R-32/152a/1234ze(E) (41.5/10.0/48.5) | HFC/HFO | A2L | 295.92 | 295.24 | replacement for R-22/R-407C
445A | R-744/134a/1234ze(E) (6.0/9.0/85.0) | HFC/HFO | A2L | 134.71 | 117.91 | replacement for R-134a in mobile air-conditioning
446A | R-32/1234ze(E)/600 (68.0/29.0/3.0) | HFC/HFO | A2L | 461.15 | 460.77 | replacement for R-410A in stationary air-conditioners
447A | R-32/125/1234ze(E) (68.0/3.5/28.5) | HFC/HFO | A2L | 583.495 | 571.595 | replacement for R-410A in stationary air-conditioners
447B | R-32/125/1234ze (E) (68.0/8.0/24.0) | HFC/HFO | A2L | 740.68 | 714.2 | replacement for R-410A in stationary air-conditioners
448A | R-32/125/1234yf/134a/1234ze(E) (26.0/26.0/20.0/21.0/7.0) | HFC/HFO | A1 | 1387.09 | 1273.49 | non-flammable replacement for 404A in low and medium temperature commercial and transport refrigeration.
449A | R-32 /125 /1234yf /134a (24.3/24.7/25.3/25.7) | HFC/HFO | A1 | 1397.047 | 1281.854 | non-flammable replacement for 404A in low and medium temperature commercial and transport refrigeration.
449B | R-32/125/1234yf/134a (25.2/24.3/23.2/27.3) | HFC/HFO | A1 | 1411.918 | 1296.046 | non-flammable replacement for 404A in low and medium temperature commercial and transport refrigeration.
449C | R-32/125/1234yf/134a (20.0/20.0/31.0/29.0) | HFC/HFO | A1 | 1250.94 | 1146.71 | non-flammable replacement for 404A
450A | R-134a/1234ze(E) (42.0/58.0) | HFC/HFO | A1 | 604.66 | 546.58 | non-flammable replacement for R-134a in medium temperature commercial refrigeration
451A | R-1234yf/134a (89.8/10.2) | HFC/HFO | A2L | 149.452 | 133.498 | replacement for R-134a
451B | R-1234yf/134a (88.8/11.2) | HFC/HFO | A2L | 163.712 | 146.488 | replacement for R-134a
452A | R-32/125/1234yf (11.0/59.0/30.0 | HFC/HFO | A1 | 2140.45 | 1945.07 | non-flammable replacement for 404A in low and medium temperature commercial and transport refrigeration.
452B | R-32/125/1234yf (67.0/7.0/26.0) | HFC/HFO | A2L | 698.29 | 675.75 | replacement for R-410A in chillers
452C | R-32/125/1234yf (12.5/61.0/26.5) | HFC/HFO | A1 | 2220.435 | 2018.59 | non-flammable replacement for 404A in low and medium temperature commercial refrigeration .
453A | R-32/125/134a/227ea/600/601a (20.0/20.0/53.8/5.0/0.6/0.6) | HFC | A1 | 1765.394 | 1636.354 | non-flammable retrofit replacement for R-22 for air-conditioning and refrigeration applications
454A | R-32/1234yf (35.0/65.0) | HFC/HFO | A2L | 238.85 | 237.6 | replacement for 404A in low and medium temperature commercial refrigeration.
454B | R-32/1234yf (68.9/31.1) | HFC/HFO | A2L | 466.319 | 466.764 | replacement for R-410A
454C | R-32/1234yf (21.5/78.5) | HFC/HFO | A2L | 148.265 | 146.34 | replacement for 404A in low and medium temperature commercial refrigeration (hermetic units).
455A | R-744/32/1234yf (3.0/21.5/75.5) | HFC/HFO | A2L | 148.175 | 146.34 | replacement for 404A in low and medium temperature commercial refrigeration (hermetic units).
456A | R-32/134a/1234ze(E) (6.0/45.0/49.0) | HFC/HFO | A1 | 687.43 | 626.11 | non-flammable replacement for R-134a in medium temperature commercial refrigeration
457A | R-32/1234yf/152a (18.0/70.0/12.0) | HFC/HFO | A2L | 139.18 | 139.12 | replacement for 404A in low and medium temperature commercial refrigeration.
458A | R-32/125/134a/227ea/236fa (20.5/4.0/61.4/13.5/0.6) | HFC | A1 | 1649.955 | 1564.395 | non-flammable replacement for R-22
459A | R-32/1234yf/1234ze(E) (68.0/26.0/6.0) | HFC/HFO | A2L | 460.46 | 460.68 | replacement for R-410A
459B | R-32/1234yf/1234ze(E) (21.0/69.0/10.0) | HFC/HFO | A2L | 145.21 | 142.96 | replacement for 404A in low and medium temperature commercial refrigeration.
460A | R-32/125/134a/1234ze(E) (12.0/52.0/14.0/22.0) | HFC/HFO | A1 | 2102.74 | 1911.86 | non-flammable replacement for 404A in low and medium temperature commercial refrigeration.
460B | R-32/125/134a/1234ze(E) (28.0/25.0/20.0/27.0) | HFC/HFO | A1 | 1351.89 | 1242.33 | non-flammable replacement for 404A in low and medium temperature commercial refrigeration.
460C | R-32/125/134a/1234ze(E) (2.5/2.5/46.0/49.0) | HFC/HFO | A1 | 765.605 | 694.665 | non-flammable replacement for R-134a
461A | R-125/143a/134a/227ea/600a (55.0/5.0/32.0/5.0/3.0) | HFC | A1 | 2767.19 | 2567.09
462A | R-32/125/143a/134a/600 (9.0/42.0/2.0/44.0/3.0) | HFC | A2 | 2249.47 | 2060.45
463A | R-744/32/125/1234yf/134a (6/36/30/14/14) | HFC/HFO | A1 | 1493.82 | 1376.92
464A | R-32/125/1234ze(E)/227ea (27/27/40/6) | HFC/HFO | A1 | 1323.25 | 1240.09 | non-flammable replacement for R-404A
465A | R-32/290/1234yf (21.0/7.9/71.1) | HFC/HFO | A2 | 144.831 | 143.118
466A | R-32/125/13I1 (49.0/11.5/39.5) | HFC/IFC | A1 | 733.25 | 696.28 | non-flammable replacement for R-410A in stationary residential and commercial air-conditioning
467A | R-32/125/134a/600a (22.0/5.0/72.4/0.6) | HFC/HC | A2L | 1358.838 | 1248.658
468A | R-1132a/32/1234yf (3.5/21.5/75.0) | HFC/HFO | A2L | 148.125 | 146.34
469A | R-744/32/125 (35.0/32.5/32.5) | HFC | A1 | 1357.225 | 1250.625 | non-flammable replacement for R-23 for very low temperature applications
470A | R-744/32/125/134a/1234ze(E)/227ea (10/17/19/7/44/3) | HFC/HFO | A1 | 979.63 | 909.43 | non-flammable replacement for R-410A
470B | R-744/32/125/134a/1234ze(E)/227ea (10/11.5/11.5/3/57/7) | HFC/HFO | A1 | 752.515 | 716.575 | non-flammable replacement for R-404A and R-507
Azeotropes
507A | R-125/143a (50.0/50.0) | HFC | A1 | 3985 | 3985 | medium and low temperature commercial refrigeration;F-Gas Regulation use restrictions
508A | R-23/116 (39.0/61.0) | PFC/HFC | A1 | 13214 | 11607 | very low temperature refrigeration
508B | R-23/116 (46.0/54.0) | PFC/HFC | A1 | 13396 | 11698 | very low temperature refrigeration
512A | R-134a/152a (5.0/95.0) | HFC | A2 | 189.3 | 196.1 | replacement for R-134a
513A | R-1234yf/134a (56.0/44.0) | HFC/HFO | A1 | 631.44 | 572.56 | non-flammable replacement for R-134a in medium temperature commercial refrigeration and chillers
513B | R-1234yf/134a (58.5/41.5) | HFC/HFO | A1 | 595.79 | 540.085 | non-flammable replacement for R-134a in medium temperature commercial refrigeration and chillers
514A | R-1336mzz-Z/1130(E) [trans-1,2dichloroethylene (t-DCE)] | HFO/HCO | B1 | 6.723 | 1.5 | non-flammable replacement for R-123 in low pressure centrifugal chillers
515A | R-1234ze (E)/227ea (88.0/12.0) | HFC/HFO | A1 | 392.56 | 402.88 | non-flammable replacement for R-134a, proposed for flooded chillers
515B | R-1234ze (E)/227ea (91.1/8.9) | HFC/HFO | A1 | 292.957 | 299.061 | non-flammable replacement for R-134a in medium and high temperature commercial refrigeration
516A | R-1234yf/134a/152a (77.5/8.5/14.0) | HFC/HFO | A2L | 142.01 | 130.595 | replacement for R-134a in medium temperature commercial refrigeration, heat pumps and chillers
Notes on refrigerant type: The safety properties (flammability) of refrigerants categorised as HC/HFC are determined by the HCs. Some refrigerants contain only small quantities of HCs and are not categorised as HCs in this table. All HFC, HC/HFC, PFC/HFC, HFC/HFO and HFC/IFC refrigerants are subject to the F-Gas Regulation. HFC/HFO refrigerants typically have lower GWPs that the HFCs they are intended to replace. R-514A is not subject to the F-Gas Regulation except for the HFO component which is subject to reporting. Notes on Safety Classification: ASHRAE Standard 34 and ISO 817 defines two safety classifications for toxicity. Class A denotes refrigerants of lower toxicity, and class B denotes refrigerants of higher toxicity. For flammability, there are four classifications. These are class 1, for refrigerants that do not propagate a flame when tested as per the standard; class 2, for refrigerants of lower flammability; Class 2L, for flammable refrigerants that burn very slowly and class 3, for highly flammable refrigerants such as the hydrocarbons. Notes on GWP:F-Gas Regulation 517/2014 uses AR4 GWP values where available. GWP values have been reviewed since then by IPCC and AR5 values are also shown. In particular GWP values for the HFOs listed are <1, but for these calculations a value of 1 is used. See GWP calculations sheet for further explanation.

## GWP calculations
Refrigerants subject to the F-Gas Regulation 517/2014 |  |  |  | Component GWPs and Refrigerant Composition
March 2020 | This list is not intended to be complete or definitive. Please refer to the latest edition of ASHRAE Standard 34 and all published addenda or the latest edition of ISO 817 and its amendments for complete information on refrigerant designations and safety classifications. |  |  | 23 | 32 | 125 | 134a | 143a | 152a | 227ea | 236fa | 1234ze(E) | 1234yf | 1336mzz(Z) | 116 | 218 | 290 | 600 | 600a | 601 | 601a | E170 | 744 | 13I1 | 1132a | 1130(E) | GWP Source see notes on GWP Calculations
Number | Refrigerant Composition (Mass % ) | GWP F-Gas AR4 | GWP AR5 | 14800 | 675 | 3500 | 1430 | 4470 | 124 | 3220 | 9810 | 7 | 4 | 9 | 12200 | 8830 | 3 | 4 | 3 | 5 | 5 | 0 | 1 | 0 | 0 | 0 | F-Gas
|  |  |  | 12400 | 677 | 3170 | 1300 | 4800 | 138 | 3350 | 8060 | 1 | 1 | 2 | 11100 | 8900 | 3 | 4 | 3 | 5 | 5 | 1 | 1 | 0 | 1 | 0 | AR5
Zeotropes | [11 empty] | <1 | <1 | [8 empty] | 1 |  |  |  | no AR5 value | HFOs (AR5) E170(TAR) | Composition Check
404A | R-125/143a/134a (44.0/52.0/4.0) | 3921.6 | 3942.8 |  |  | 44 | 4 | 52 | [19 empty] | 100
407A | R-32/125/134a (20.0/40.0/40.0) | 2107 | 1923.4 |  | 20 | 40 | 40 | [20 empty] | 100
407B | R-32/125/134a (10.0/70.0/20.0) | 2803.5 | 2546.7 |  | 10 | 70 | 20 | [20 empty] | 100
407C | R-32/125/134a (23.0/25.0/52.0) | 1773.85 | 1624.21 |  | 23 | 25 | 52 | [20 empty] | 100
407D | R-32/125/134a (15.0/15.0/70.0) | 1627.25 | 1487.05 |  | 15 | 15 | 70 | [20 empty] | 100
407E | R-32/125/134a (25.0/15.0/60.0) | 1551.75 | 1424.75 |  | 25 | 15 | 60 | [20 empty] | 100
407F | R-32/125/134a (30.0/30.0/40.0) | 1824.5 | 1674.1 |  | 30 | 30 | 40 | [20 empty] | 100
407G | R-32/125/134a (2.5/2.5/95.0) | 1462.875 | 1331.175 |  | 2.5 | 2.5 | 95 | [20 empty] | 100
407H | R-32/125/134a (32.5/15.0/52.5) | 1495.125 | 1378.025 |  | 32.5 | 15 | 52.5 | [20 empty] | 100
410A | R-32/125 (50.0/50.0) | 2087.5 | 1923.5 |  | 50 | 50 | [21 empty] | 100
410B | R-32/125 (45.0/55.0) | 2228.75 | 2048.15 |  | 45 | 55 | [21 empty] | 100
413A | R-218/134a/600a (9.0/88.0/3.0) | 2053.19 | 1945.09 |  |  |  | 88 | [8 empty] | 9 |  |  | 3 | [8 empty] | 100
417A | R-125/134a/600 (46.6/50.0/3.4) | 2346.136 | 2127.356 |  |  | 46.6 | 50 | [10 empty] | 3.4 | [9 empty] | 100
417B | R-125/134a/600 (79.0/18.3/2.7) | 3026.798 | 2742.308 |  |  | 79 | 18.3 | [10 empty] | 2.7 | [9 empty] | 100
417C | R-125/134a/600 (19.5/78.8/1.7) | 1809.408 | 1642.618 |  |  | 19.5 | 78.8 | [10 empty] | 1.7 | [9 empty] | 100
419A | R-125/134a/E170 (77.0/19.0/4.0) | 2966.7 | 2687.94 |  |  | 77 | 19 | [14 empty] | 4 | [5 empty] | 100
419B | R-125/134a/E170 (48.5/48.0/3.5) | 2383.9 | 2161.485 |  |  | 48.5 | 48 | [14 empty] | 3.5 | [5 empty] | 100
421A | R-125/134a (58.0/42.0) | 2630.6 | 2384.6 |  |  | 58 | 42 | [20 empty] | 100
421B | R-125/134a (85.0/15.0) | 3189.5 | 2889.5 |  |  | 85 | 15 | [20 empty] | 100
422A | R-125/134a/600a (85.1/11.5/3.4) | 3143.052 | 2847.272 |  |  | 85.1 | 11.5 | [11 empty] | 3.4 | [8 empty] | 100
422B | R-125/134a/600a (55.0/42.0/3.0) | 2525.69 | 2289.59 |  |  | 55 | 42 | [11 empty] | 3 | [8 empty] | 100
422C | R-125/134a/600a (82.0/15.0/3.0) | 3084.59 | 2794.49 |  |  | 82 | 15 | [11 empty] | 3 | [8 empty] | 100
422D | R-125/134a/600a (65.1/31.5/3.4) | 2729.052 | 2473.272 |  |  | 65.1 | 31.5 | [11 empty] | 3.4 | [8 empty] | 100
422E | R-125/134a/600a (58.0/39.3/2.7) | 2592.071 | 2349.581 |  |  | 58 | 39.3 | [11 empty] | 2.7 | [8 empty] | 100
423A | R-134a/227ea (52.5/47.5) | 2280.25 | 2273.75 |  |  |  | 52.5 |  |  | 47.5 | [17 empty] | 100
424A | R-125/134a/600a/600/601a (50.5/47.0/0.9/1.0/0.6) | 2439.697 | 2211.947 |  |  | 50.5 | 47 | [10 empty] | 1 | 0.9 |  | 0.6 | [6 empty] | 100
425A | R-32/134a/227ea (18.5/69.5/12) | 1505.125 | 1430.745 |  | 18.5 |  | 69.5 |  |  | 12 | [17 empty] | 100
426A | R-125/134a/600/601a (5.1/93.0/1.3/0.6) | 1508.482 | 1370.752 |  |  | 5.1 | 93 | [10 empty] | 1.3 |  |  | 0.6 | [6 empty] | 100
427A | R-32/125/143a/134a (15.0/25.0/10.0/50.0) | 2138.25 | 2024.05 |  | 15 | 25 | 50 | 10 | [19 empty] | 100
428A | R-125/143a/290/600a (77.5/20.0/0.6/1.9) | 3606.575 | 3416.825 |  |  | 77.5 |  | 20 | [8 empty] | 0.6 |  | 1.9 | [8 empty] | 100
429A | R-E170/152a/600a (60.0/10.0/30.0) | 13.3 | 15.3 | [5 empty] | 10 | [9 empty] | 30 |  |  | 60 | [5 empty] | 100
430A | R-152a/600a (76.0/24.0) | 94.96 | 105.6 | [5 empty] | 76 | [9 empty] | 24 | [8 empty] | 100
431A | R-290/152a (71.0/29.0) | 38.09 | 42.15 | [5 empty] | 29 | [7 empty] | 71 | [10 empty] | 100
434A | R-125/143a/134a/600a (63.2/18.0/16.0/2.8) | 3245.484 | 3075.524 |  |  | 63.2 | 16 | 18 | [10 empty] | 2.8 | [8 empty] | 100
435A | R-E170/152a (80.0/20.0) | 24.8 | 28.4 | [5 empty] | 20 | [12 empty] | 80 | [5 empty] | 100
437A | R-125/134a/600/601 (19.5/78.5/1.4/0.6) | 1805.136 | 1638.736 |  |  | 19.5 | 78.5 | [10 empty] | 1.4 |  |  | 0.6 | [6 empty] | 100
438A | R-32/125/134a/600/601a (8.5/45.0/44.2/1.7/0.6) | 2264.533 | 2058.743 |  | 8.5 | 45 | 44.2 | [10 empty] | 1.7 |  |  | 0.6 | [6 empty] | 100
439A | R-32/125/600a (50.0/47.0/3.0) | 1982.59 | 1828.49 |  | 50 | 47 | [12 empty] | 3 | [8 empty] | 100
440A | R-290/134a/152a (0.6/1.6/97.8) | 144.17 | 155.782 |  |  |  | 1.6 |  | 97.8 | [7 empty] | 0.6 | [10 empty] | 100
442A | R-32/125/134a/152a/227ea (31.0/31.0/30.0/3.0/5.0) | 1887.97 | 1754.21 |  | 31 | 31 | 30 |  | 3 | 5 | [17 empty] | 100
444A | R-32/152a/1234ze(E) (12.0/5.0/83.0) | 93.01 | 88.97 |  | 12 |  |  |  | 5 |  |  | 83 | [15 empty] | 100
444B | R-32/152a/1234ze(E) (41.5/10.0/48.5) | 295.92 | 295.24 |  | 41.5 |  |  |  | 10 |  |  | 48.5 | [15 empty] | 100
445A | R-744/134a/1234ze(E) (6.0/9.0/85.0) | 134.71 | 117.91 |  |  |  | 9 |  |  |  |  | 85 | [10 empty] | 6 |  |  |  |  | 100
446A | R-32/1234ze(E)/600 (68.0/29.0/3.0) | 461.15 | 460.77 |  | 68 | [6 empty] | 29 | [5 empty] | 3 | [9 empty] | 100
447A | R-32/125/1234ze(E) (68.0/3.5/28.5) | 583.495 | 571.595 |  | 68 | 3.5 | [5 empty] | 28.5 | [15 empty] | 100
447B | R-32/125/1234ze (E) (68.0/8.0/24.0) | 740.68 | 714.2 |  | 68 | 8 | [5 empty] | 24 | [15 empty] | 100
448A | R-32/125/1234yf/134a/1234ze(E) (26.0/26.0/20.0/21.0/7.0) | 1387.09 | 1273.49 |  | 26 | 26 | 21 |  |  |  |  | 7 | 20 | [14 empty] | 100
449A | R-32 /125 /1234yf /134a (24.3/24.7/25.3/25.7) | 1397.047 | 1281.854 |  | 24.3 | 24.7 | 25.7 | [5 empty] | 25.3 | [14 empty] | 100
449B | R-32/125/1234yf/134a (25.2/24.3/23.2/27.3) | 1411.918 | 1296.046 |  | 25.2 | 24.3 | 27.3 | [5 empty] | 23.2 | [14 empty] | 100
449C | R-32/125/1234yf/134a (20.0/20.0/31.0/29.0) | 1250.94 | 1146.71 |  | 20 | 20 | 29 | [5 empty] | 31 | [14 empty] | 100
450A | R-134a/1234ze(E) (42.0/58.0) | 604.66 | 546.58 |  |  |  | 42 |  |  |  |  | 58 | [15 empty] | 100
451A | R-1234yf/134a (89.8/10.2) | 149.452 | 133.498 |  |  |  | 10.2 | [5 empty] | 89.8 | [14 empty] | 100
451B | R-1234yf/134a (88.8/11.2) | 163.712 | 146.488 |  |  |  | 11.2 | [5 empty] | 88.8 | [14 empty] | 100
452A | R-32/125/1234yf (11.0/59.0/30.0 | 2140.45 | 1945.07 |  | 11 | 59 | [6 empty] | 30 | [14 empty] | 100
452B | R-32/125/1234yf (67.0/7.0/26.0) | 698.29 | 675.75 |  | 67 | 7 | [6 empty] | 26 | [14 empty] | 100
452C | R-32/125/1234yf (12.5/61.0/26.5) | 2220.435 | 2018.59 |  | 12.5 | 61 | [6 empty] | 26.5 | [14 empty] | 100
453A | R-32/125/134a/227ea/600/601a (20.0/20.0/53.8/5.0/0.6/0.6) | 1765.394 | 1636.354 |  | 20 | 20 | 53.8 |  |  | 5 | [7 empty] | 0.6 |  |  | 0.6 | [6 empty] | 100
454A | R-32/1234yf (35.0/65.0) | 238.85 | 237.6 |  | 35 | [7 empty] | 65 | [14 empty] | 100
454B | R-32/1234yf (68.9/31.1) | 466.319 | 466.764 |  | 68.9 | [7 empty] | 31.1 | [14 empty] | 100
454C | R-32/1234yf (21.5/78.5) | 148.265 | 146.34 |  | 21.5 | [7 empty] | 78.5 | [14 empty] | 100
455A | R-744/32/1234yf (3.0/21.5/75.5) | 148.175 | 146.34 |  | 21.5 | [7 empty] | 75.5 | [9 empty] | 3 |  |  |  |  | 100
456A | R-32/134a/1234ze(E) (6.0/45.0/49.0) | 687.43 | 626.11 |  | 6 |  | 45 |  |  |  |  | 49 | [15 empty] | 100
457A | R-32/1234yf/152a (18.0/70.0/12.0) | 139.18 | 139.12 |  | 18 |  |  |  | 12 |  |  |  | 70 | [14 empty] | 100
458A | R-32/125/134a/227ea/236fa (20.5/4.0/61.4/13.5/0.6) | 1649.955 | 1564.395 |  | 20.5 | 4 | 61.4 |  |  | 13.5 | 0.6 | [16 empty] | 100
459A | R-32/1234yf/1234ze(E) (68.0/26.0/6.0) | 460.46 | 460.68 |  | 68 | [6 empty] | 6 | 26 | [14 empty] | 100
459B | R-32/1234yf/1234ze(E) (21.0/69.0/10.0) | 145.21 | 142.96 |  | 21 | [6 empty] | 10 | 69 | [14 empty] | 100
460A | R-32/125/134a/1234ze(E) (12.0/52.0/14.0/22.0) | 2102.74 | 1911.86 |  | 12 | 52 | 14 |  |  |  |  | 22 | [15 empty] | 100
460B | R-32/125/134a/1234ze(E) (28.0/25.0/20.0/27.0) | 1351.89 | 1242.33 |  | 28 | 25 | 20 |  |  |  |  | 27 | [15 empty] | 100
460C | R-32/125/134a/1234ze(E) (2.5/2.5/46.0/49.0) | 765.605 | 694.665 |  | 2.5 | 2.5 | 46 |  |  |  |  | 49 | [15 empty] | 100
461A | R-125/143a/134a/227ea/600a (55.0/5.0/32.0/5.0/3.0) | 2767.19 | 2567.09 |  |  | 55 | 32 | 5 |  | 5 | [8 empty] | 3 | [8 empty] | 100
462A | R-32/125/143a/134a/600 (9.0/42.0/2.0/44.0/3.0) | 2249.47 | 2060.45 |  | 9 | 42 | 44 | 2 | [9 empty] | 3 | [9 empty] | 100
463A | R-744/32/125/1234yf/134a (6/36/30/14/14) | 1493.82 | 1376.92 |  | 36 | 30 | 14 | [5 empty] | 14 | [9 empty] | 6 |  |  |  |  | 100
464A | R-32/125/1234ze(E)/227ea (27/27/40/6) | 1323.25 | 1240.09 |  | 27 | 27 |  |  |  | 6 |  | 40 | [15 empty] | 100
465A | R-32/290/1234yf (21.0/7.9/71.1) | 144.831 | 143.118 |  | 21 | [7 empty] | 71.1 |  |  |  | 7.9 | [10 empty] | 100
466A | R-32/125/13I1 (49.0/11.5/39.5) | 733.25 | 696.28 |  | 49 | 11.5 | [17 empty] | 39.5 |  |  |  | 100
467A | R-32/125/134a/600a (22.0/5.0/72.4/0.6) | 1358.838 | 1248.658 |  | 22 | 5 | 72.4 | [11 empty] | 0.6 | [8 empty] | 100
468A | R-1132a/32/1234yf (3.5/21.5/75.0) | 148.125 | 146.34 |  | 21.5 | [7 empty] | 75 | [11 empty] | 3.5 |  |  | 100
469A | R-744/32/125 (35.0/32.5/32.5) | 1357.225 | 1250.625 |  | 32.5 | 32.5 | [16 empty] | 35 |  |  |  |  | 100
470A | R-744/32/125/134a/1234ze(E)/227ea (10/17/19/7/44/3) | 979.63 | 909.43 |  | 17 | 19 | 7 |  |  | 3 |  | 44 | [10 empty] | 10 |  |  |  |  | 100
470B | R-744/32/125/134a/1234ze(E)/227ea (10/11.5/11.5/3/57/7) | 752.515 | 716.575 |  | 11.5 | 11.5 | 3 |  |  | 7 |  | 57 | [10 empty] | 10 |  |  |  |  | 100
Azeotropes
507A | R-125/143a (50.0/50.0) | 3985 | 3985 |  |  | 50 |  | 50 | [19 empty] | 100
508A | R-23/116 (39.0/61.0) | 13214 | 11607 | 39 | [10 empty] | 61 | [12 empty] | 100
508B | R-23/116 (46.0/54.0) | 13396 | 11698 | 46 | [10 empty] | 54 | [12 empty] | 100
512A | R-134a/152a (5.0/95.0) | 189.3 | 196.1 |  |  |  | 5 |  | 95 | [18 empty] | 100
513A | R-1234yf/134a (56.0/44.0) | 631.44 | 572.56 |  |  |  | 44 | [5 empty] | 56 | [14 empty] | 100
513B | R-1234yf/134a (58.5/41.5) | 595.79 | 540.085 |  |  |  | 41.5 | [5 empty] | 58.5 | [14 empty] | 100
514A | R-1336mzz(Z)/1130(E) (74.7/25.3) | 6.723 | 1.5 | [10 empty] | 74.7 | [11 empty] | 25.3 |  | 100
515A | R-1234ze (E)/227ea (88.0/12.0) | 392.56 | 402.88 | [6 empty] | 12 |  | 88 | [15 empty] | 100
515B | R-1234ze (E)/227ea (91.1/8.9) | 292.957 | 299.061 | [6 empty] | 8.9 |  | 91.1 | [15 empty] | 100
516A | R-1234yf/134a/152a (77.5/8.5/14.0) | 142.01 | 130.595 |  |  |  | 8.5 |  | 14 |  |  |  | 77.5 | [14 empty] | 100
Notes on GWP Calculations: F-Gas Regulation 517/2014 uses AR4 GWP values where available. GWP values have been reviewed since then by IPCC and AR5 values are also shown. In particular GWP values for the HFOs listed are <1, but for these calculations a value of 1 is used. R-13I1 is not listed in AR5 but more recent publication assumes it to have a neglible GWP. For the HCs the values listed in the F-Gas Regulation are used for AR5 GWP calculations. For E170 the TAR value is used for the AR5 calculation, whereas a default value of 0 is used for the F-Gas AR4 calculation.